## Slide 1: 2012 Life Safety Code
Monte Engel, PE
Director, Division of Life Safety & Construction
ND Department of Health
600 E. Boulevard Ave., Dept. 301
Bismarck, ND 58505-0200
701.328.4873
mengel@nd.gov
http://www.ndhealth.gov/LifeSafety/

## Slide 2: outline
Adoption of state construction standards.
Updates on the 2012 edition of NFPA 101.
S&C letter on door testing.
Common survey findings.
Questions?

## Slide 3: ND Administrative Code
Effective July 1, 2015
New construction standards for:
  hospitals
  nursing facilities
  basic care facilities

## Slide 4: ND Administrative Code
Hospitals:
North Dakota General Standards of Construction and Equipment for Hospitals, Chapter 33-07-02.1

## Slide 5: ND Administrative Code
Nursing Facilities:
North Dakota General Standards of Construction and Equipment for Nursing Facilities, Chapter 33-07-04.2

## Slide 6: Nd administrative code
Basic Care Facilities:
North Dakota General Standards of Construction and Equipment for Basic Care Facilities, Chapter 33-03-24.2

## Slide 7: cms
2012 edition of NFPA 101, Life Safety Code
2012 edition of NFPA 99, Health Facilities Code
  Notice of Final Rule Making: May 4, 2016
  S&C letter: June 20, 2016
  Effective Date: July 5, 2016
  Begin Surveying: November 1, 2016

## Slide 8: NFPA
Quick Compare
Life Safety Code 2000 & 2012 for Health Care
NFPA 101 Changes Affecting Your Facility
nfpacatalog.org

## Slide 9: 2012 Lsc – door locks
19.2.2.2.5.2
Provisions on door locking expanded to include locking for specialized protective measures for patient safety (e.g., infant abduction concerns); delayed egress locking provision revised to remove former limitation of one such device per egress path.

## Slide 10: 2012 Lsc – corridor projections
19.2.3.4(2)
Where corridor width is at least 6 ft, noncontinuous projections not more than 6 in from the corridor wall, above handrail height, shall be permitted.

## Slide 11: 2012 Lsc – wheeled equipment
19.2.3.4(4)
Projections into the required corridor width shall be permitted for wheeled equipment, provided that all of the following conditions are met:
  (a) The wheeled equipment does not reduce the clear and unobstructed corridor width to less than 60 in.

## Slide 12: 2012 Lsc – wheeled equipment
  19.2.3.4(4)
  (b) The fire safety plan and training program address the relocation of the wheeled equipment during a fire or similar emergency.

## Slide 13: 2012 Lsc – wheeled equipment
  19.2.3.4(4)
  (c) The wheeled equipment is limited to the following:
    i. Equipment in use and carts in use
    ii. Medical emergency equipment not in use
    iii. Patient lift and transport equipment

## Slide 14: 2012 Lsc – fixed furniture
19.2.3.4(5)
Where the corridor width is at least 8 ft, projections into the required width shall be permitted for fixed furniture, provided that all of the following conditions are met:
  (a) The furniture is securely attached to the floor or the wall.
  (b) The furniture does not reduce the corridor width to less than 6 ft.

## Slide 15: 2012 Lsc – fixed furniture
19.2.3.4(5)
  (c) The furniture is located only on one side of the corridor.
  (d) The furniture is grouped such that each grouping does not exceed an area of 50 sq ft.
  (e) The furniture groupings are separated from each other by a distance of at least 10 ft.

## Slide 16: 2012 Lsc – fixed furniture
  19.2.3.4(5)
    (f) The furniture does not obstruct access to building service and fire protection equipment.
    (g) Corridors throughout the smoke compartment are protected by a smoke detection system or the furniture is located to allow direct supervision from a nurses’ station.
    (h) The smoke compartment is protected throughout by an approved, supervised automatic sprinkler system.

## Slide 17: 2012 Lsc – sleeping suites
19.2.5.7.2.2
  (A) Sleeping suites of more than 1000 sq ft shall have not less than two exit access doors located remotely from each other.
  (B) One means of egress from the suite shall be directly to a corridor.
  (C) One means of egress from the suite can be to another suite.

## Slide 18: 2012 Lsc – cooking facilities
19.3.2.5.3
Within a smoke compartment, where residential or commercial cooking equipment is used to prepare meals for 30 or fewer persons, one cooking facility shall be permitted to be open to the corridor, provided all the following conditions are met:

## Slide 19: 2012 Lsc – cooking facilities
  19.3.2.5.3
  (1) The portion of the building served by the cooking facility is limited to 30 beds and is separated from other portions by a smoke barrier.
  (2) The cooktop or range is equipped with a range hood the width of the cooking surface and grease baffles.
  (3) The hood system has a minimum airflow of 500 cfm.

## Slide 20: 2012 Lsc – cooking facilities
  19.3.2.5.3
  (4) The hood system (if not ducted to the exterior) has a charcoal filter.
  (5) The cooktop or range is equipped with:
    (a) A fire suppression system complying with UL 300 or UL 300A.
    (b) A manual release of the extinguishing system complying with NFPA 96.
    (c) An interlock to turn off all sources of fuel and electricity when the suppression system is activated.

## Slide 21: 2012 Lsc – cooking facilities
  19.3.2.5.3
  (6) The use of solid fuel for cooking is prohibited.
  (7) Deep-fat frying is prohibited.
  (8) Portable fire extinguishers are provided.

## Slide 22: 2012 Lsc – cooking facilities
  19.3.2.5.3
  (9) A switch is provided:
    (a) A locked switch or one in a restricted area, is provided to deactivate the cooktop or range.
    (b) The switch is used to deactivate the cooktop or range whenever staff are not present.
    (c) The switch is on a timer, not exceeding 120 minutes.

## Slide 23: 2012 Lsc – cooking facilities
  19.3.2.5.3
  (10) Use, inspection, testing, and maintenance complies with NFPA 96.
  (11) Not less than two smoke alarms are located not closer than 20 ft from the cooktop or range.
  (12) No smoke detector is located less than 20 ft from the cooktop or range.
  (13) The smoke compartment has a sprinkler system.

## Slide 24: 2012 lsc – clothes closets
19.3.5.10
Sprinklers are not required in clothes closets of patient sleeping rooms in hospitals where the area of the closet does not exceed 6 sq ft, provided the distance from the sprinkler in the room to the back wall of the closet does not exceed the maximum permitted by NFPA 13.

## Slide 25: 2012 Lsc - fireplaces
19.5.2.3(2)
Direct-vent gas fireplaces (NFPA 54) are permitted in smoke compartment containing sleeping rooms, provided all the following are met:
  (a) Installed, maintained, and used in compliance with 9.2.2.
  (b) The fireplace is not located inside a sleeping room.

## Slide 26: 2012 Lsc - fireplaces
  19.5.2.3(2)
  (c) The smoke compartment has an automatic sprinkler system.
  (d) The fireplace has a sealed glass front with a wire mesh panel or screen.
  (e) The controls are locked or located in a restricted location.
  (f) Carbon monoxide detection is provided in the room where the fireplace is located.

## Slide 27: 2012 Lsc - fireplaces
19.5.2.3(3)
Solid fuel-burning fireplaces are allowed in other than sleeping areas:
  (a) The area is separated from sleeping spaces with 1-hr rating.
  (b) The fireplace complies with 9.2.2.
  (c) The fireplace is equipped with heat-tempered glass rated 650˚F.
  (d) Carbon monoxide detection is provided in the room.

## Slide 28: 2012 Lsc - draperies
19.7.5.1
Draperies, curtains, and other loosely hanging fabrics and films serving as furnishings or decorations shall comply with 10.3.1.
  (3) Does not include draperies and curtains in windows of patient sleeping rooms in smoke compartments with a sprinkler system.

## Slide 29: 2012 Lsc - decorations
19.7.5.6
Combustible decorations:
Flame-retardant or treated with a flame-retardant coating.
Meet NFPA 701.
Heat release not exceeding 100 kW per NFPA 289.

## Slide 30: 2012 Lsc - decorations
19.7.5.6
(4) The decorations, such as photographs, paintings and other art, are attached directly to the walls, ceiling, and non-fire rated doors:
  Decorations on doors do not interfere with the latching operation.
  Decorations do not exceed 20% of the wall, ceiling, and doors in a room in a smoke compartment that is not protected with a sprinkler system.

## Slide 31: 2012 Lsc - decorations
  19.7.5.6
  (c) Decorations do not exceed 30% of the wall, ceiling, and doors in a room in a smoke compartment that is protected with a sprinkler system.
  (d) Decorations do not exceed 50% of the wall, ceiling, and doors in a patient sleeping room in a smoke compartment that is protected with a sprinkler system.

## Slide 32: 2012 Lsc - containers
19.7.5.7.2
Containers used solely for recycling clean waste or for patient records awaiting destruction may be increased in size to 96 gallons.

## Slide 33: 2012 lsc - miscellaneous
More restrictive standards:
Quarterly fire hose valve inspections.
5-year internal inspections of the sprinkler pipe.

## Slide 34: 2012 lsc - miscellaneous
Less restrictive standards:
Monthly fire pump testing rather than weekly.
Semi-annual water-flow switch testing rather than quarterly.

## Slide 35: 2012 lsc – Chapter 43
Building Rehabilitation- Modifications – Renovations – Additions
Repairs and Change of Use are now governed by Chapter 43 Building Rehabilitation.
This chapter provides direction on when New and Existing Chapters are required, or which new chapter requirements are to be applied.

## Slide 36: 2012 lsc – Door testing
S&C 17-38-LSC
Fire door assemblies are required to be annually inspected and tested in accordance with NFPA 80.
Compliance with the annual fire door assembly inspection and testing is required by January 1, 2018.

## Slide 37: 2012 lsc – Door testing
Non-rated door assemblies, including corridor doors to resident rooms and smoke barrier doors, are not subject to annual inspection and testing.
Non-rated doors should be routinely inspected as part of the facility maintenance program.

## Slide 38: 2012 lsc – fire door inspections
The requirements for the annual inspection include:
Is the door and frame free from holes and breaks in any surface?
Are all the glazing, vision light frames and glazing beads intact and securely fastened?
Are the doors, hinges, frame, hardware and threshold secure, aligned and in working order with no visible signs of damage?

## Slide 39: 2012 lsc – fire door inspections
Are there any missing or broken parts?
Is the clearance from the door edge to the frame no more than 1/8 inch?
Is the door undercut no more than ¾ inch?
Does the active door leaf completely close when operated from the full open position?

## Slide 40: 2012 lsc – fire door inspections
Does the inactive leaf close before the active leaf?
Does the latching hardware operate and secure the door in the closed position?
Is the door assembly free from any auxiliary hardware items which could interfere with its operation?
Has the door been modified since it was originally installed?
Are the gasketing and edge seals verified for integrity and operation?

## Slide 41: Common deficiencies
K0347 Smoke Detection
Smoke detectors located within 3’ of air supply diffusers or return air grills.
Notes: Cited 17 times since November 1, 2016.

## Slide 42: Common deficiencies
K0353 Sprinkler System – Maintenance and Testing
Intermediate-temperature sprinklers required in walk-in coolers/freezers with automatic defrost.
Missing ceiling tiles or holes in ceiling.
Foreign substance or corrosion on sprinklers.

## Slide 43: Common deficiencies
K0353 Sprinkler System – Maintenance and Testing
Quarterly or annual sprinkler system testing not performed.
No hydraulic nameplate.
Wrong temperature sprinklers installed.

## Slide 44: Common deficiencies
K0353 Sprinkler System – Maintenance and Testing
Control valves and gauges not inspected quarterly.
Dry sprinklers not tested/replaced in last 10 years.
Check valve/internal inspection not done in 5 years.
Gauge not recalibrated/replaced in last 5 years.

## Slide 45: Common deficiencies
K0271 Discharge from Exits
Exit discharge is not a hard, level surface of asphalt or concrete.

## Slide 46: Common deficiencies
K0345 Fire Alarm System – Testing and Maintenance
Locking device not installed on fire alarm circuit.
Semi-annual load voltage test of batteries not done.
Annual fire alarm testing not performed.
Detectors failed and not replaced.
Fire alarm system batteries not replaced in 5 years.

## Slide 47: Common deficiencies
K0712 Fire Drills
Fire drill times not varied.
Fire drills not conducted at once per shift per quarter.

## Slide 48: Questions?